## Slide 1: shear

## Slide 2: introduction
A CONCRETE BEAM SUBJECT TO A LARGE LOAD NEAR THE SUPPORTS MAY FAIL AS A RESULT OF SHEAR.
SHEAR FAILURES ARE CHARACTERISED BY SMALL DEFLECTIONS AND LACK OF DUCTILITY.
THE DESIGN SHEAR FORCE, VEd, IS NORMALLY DETERMINED AT A DISTANCE ‘d’ FROM THE FACE OF SUPPORTS.

## Slide 3: SHEAR STRENGTH
THE SHEAR STRENGTH OF A REINFORCED CONCRETE BEAM IS A FUNCTION OF
CONCRETE IN THE COMPRESSION ZONE
AGGREGATE INTERLOCK
DOWELL ACTION

## Slide 4: SHEAR RESISTANCE OF CONCRETE
THE DESIGN SHEAR RESISTANCE OF THE CONCRETE ALONE, VRd,c, IS GIVEN BY
VRd,c = [CRd,c k (100ρ1fck)⅓ + k1σcp)bwd  (min + k1σcp)bwd ------(1) (Expression 6.2a/b)
where
CRd,c = 0.18/C
k = 1 + √(200/d) ≤ 2.0
1 = Asl/bd
Asl is the area of the tensile reinforcement
cp = NEd/Ac ≤ 0.2fcd, in which NEd is the axial force in the x-section
min = 0.035k3/2fck1/2

## Slide 5: Design criterion
IF VEd < VRd,c - THE MEMBER SHOULD NOT EXPERIENCE SHEAR FAILURE
IF VEd > VRd,c - SHEAR FAILURE IS A POSSIBILITY

## Slide 6: MECHANISMS OF SHEAR FAILURE
THERE ARE TWO PRINCIPAL MECHANISMS OF SHEAR FAILURE
(i) DIAGONAL TENSION – PREVENTED BY PROVIDING SHEAR REINFORCEMENT
(ii) DIAGONAL COMPRESSION – PREVENTED BY CHECKING THE SHEAR RESISTANCE OF THE CONCRETE IS ADEQUATE
(i) (ii)

## Slide 7: Concrete strut capacity, vRd,max
The concrete strut capacity is given by Expression 6.9 in EC2
------- (2)
where
 is the strut angle: 2.5 ≤ cot  ≤ 1
 = 0.6(1 – fck/250) for fck ≤ 50 N/mm2
z  0.9d
fcd = ccfck/C (cc = 1.0 for shear)

## Slide 8: STRUT ANGLE
Use of this expression requires a value for the strut angle which, in turn, is a function of the applied shear force. Using the identity
--------------(3)
expression (2) can be transposed to make the concrete strut angle the subject of the formula as follows
------------(4)
Expression (4) can be used to calculate the strut angle by equating VRd,max = VEd

## Slide 9: SHEAR RESISTANCE OF STIRRUPS
The shear resistance of the member, controlled by yielding of the shear reinforcement, VRd,s, is given by
VRd,s ----------(5) (EXPRESSION 6.8 EC2)
where
Asw is the x-sectional area of the shear reinforcement
s is the spacing of the shear reinforcement
fywd is the design yield strength of the reinforcement

## Slide 10: TRUSS ANALOGY

## Slide 11: DESIGN PROCEDURE
The design process can be summarised as follows:
(i) Calculate the design shear force, VEd.
(ii) Determine the design shear resistance of the concrete, VRd,c, FROM (1)
(iii) If VEd < VRd,c shear reinforcement can be omitted except in beams where a minimum area of shear reinforcement must be provided (see below).

## Slide 12: DESIGN PROCEDURE (cont’D)
(iv) If VEd > VRd,c all the shear force must be resisted by the shear reinforcement. Provided VEd < VRd,max, the area of shear reinforcement can be determined using expression (5). VRd,max is estimated from (2) assuming initially cot  = 2.5. However, if the result is VEd > VRd,max a larger strut angle, , may be used. The maximum allowable value of  is 45o (i.e. cot  = 1). The actual value of the strut angle for a given design shear force, VEd, can be determined from (4) and used, in turn, to calculate the area of shear reinforcement from (5).
If the strut angle exceeds 45o, however, a deeper concrete section must be provided and steps (ii)-(iv) repeated.

## Slide 13: Minimum shear reinforcement
Minimum reinforcement, ρw, should be provided in beams where VEd < VRd,c obtained from
ρw = Asw / (sbwsin α)  ρw,min ------------(6)
where
Asw is the area of shear reinforcement within length s
s is the spacing of the shear reinforcement
bw is the breadth of the member
α = 90o for vertical stirrups  sin α = 1
ρw,min is the minimum area of shear reinforcement = (0.08fck)/fyk------------(7)

## Slide 14: Spacing of shear reinforcement (Cl. 9.2.2, EC2)
EC2 recommends that the maximum longitudinal spacing of shear reinforcement (sl,max) should not exceed
sl,max ≤ 0.75d(1 + cot ) -------(8)
where
 = 90o for vertical stirrups  cot α = 0